{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["废水"],"not_rendered":{"external_links":1,"defined_names":2},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"废水","index":0,"n_rows":6,"n_cols":18,"rows_kept":6,"merged":[[0,0,0,17],[1,5,1,17],[4,0,4,2],[5,0,5,2]],"flags":["formulas_cached_only"]}
["附件2：                惠州市2020年5月生活垃圾处理企业废水监督性监测结果（1家）"]
[{"$nulls":5},"单位:毫克/升（除PH值无量纲，粪大肠菌群为MPN/L，色度为倍外）"]
["企业名称","监测日期","监测点位","pH值","悬浮物","化学需氧量","五日生化需氧量","氨氮","总氮","总磷","总铬","六价铬","砷","镉","铅","汞","粪大肠菌群","色度"]
["惠东县垃圾填埋场","2020-04-21","废水排放口",6.93,9,16,{"v":4,"d":"4.0"},0.24,2.76,"0.01L","0.01L","0.004L","0.0003L","0.002L","0.025L","0.00004L","20L",2]
["评价",null,null,"达标","达标","达标","达标","达标","达标","达标","达标","达标","达标","达标","达标","达标","达标","达标"]
["《生活垃圾填埋场污染控制标准》GB16889-2008、广东省地方标准《水污染物排放限值》DB44/26-2001",null,null,"6—9",30,90,20,10,40,3,0.1,0.05,0.1,0.01,0.1,0.001,10000,40]