{"text_format":"3","workbook":"xlsx","n_sheets":1,"sheets":["垃圾焚烧炉废气"],"not_rendered":{"defined_names":2},"read":"whole","date_system":"1900"}

{"sheet":"垃圾焚烧炉废气","index":0,"n_rows":145,"n_cols":13,"rows_kept":145,"merged":[[0,0,0,12],[2,0,27,0],[2,1,27,1],[2,2,27,2],[2,3,27,3],[2,4,14,4],[2,5,14,5],[2,6,14,6],[2,12,27,12],[8,9,13,9],[8,10,13,10],[8,11,13,11],[12,13,16,13],[15,4,27,4],[15,5,27,5],[15,6,27,6],[21,9,26,9],[21,10,26,10],[21,11,26,11],[28,0,53,0],[28,1,53,1],[28,2,53,2],[28,3,53,3],[28,4,40,4],[28,5,40,5],[28,6,40,6],[28,12,53,12],[34,9,39,9],[34,10,39,10],[34,11,39,11],[39,13,42,13],[41,4,53,4],[41,5,53,5],[41,6,53,6],[47,9,52,9],[47,10,52,10],[47,11,52,11],[54,0,79,0],[54,1,79,1],[54,2,79,2],[54,3,79,3],[54,4,66,4],[54,5,66,5],[54,6,66,6],[54,12,79,12],[60,9,65,9],[60,10,65,10],[60,11,65,11],[65,13,66,13],[67,4,79,4],[67,5,79,5],[67,6,79,6],[73,9,78,9],[73,10,78,10],[73,11,78,11],[80,0,105,0],[80,1,105,1],[80,2,105,2],[80,3,105,3],[80,4,92,4],[80,5,92,5],[80,6,92,6],[80,12,105,12],[86,9,91,9],[86,10,91,10],[86,11,91,11],[91,13,94,13],[93,4,105,4],[93,5,105,5],[93,6,105,6],[99,9,104,9],[99,10,104,10],[99,11,104,11],[106,0,144,0],[106,1,144,1],[106,2,144,2],[106,3,144,3],[106,4,118,4],[106,5,118,5],[106,6,118,6],[106,12,144,12],[112,9,117,9],[112,10,117,10],[112,11,117,11],[119,4,131,4],[119,5,131,5],[119,6,131,6],[123,13,126,13],[125,9,130,9],[125,10,130,10],[125,11,130,11],[132,4,144,4],[132,5,144,5],[132,6,144,6],[138,9,143,9],[138,10,143,10],[138,11,143,11]]}
["附件4：          惠州市2020年6月生活垃圾处理企业废气监督性监测结果（5家）"]
["序号","企业名称","所在地","评价标准","监测点位","采样日期","烟气流量（m3/h）","监测项目","浓度","标准限值","单位","达标\n评价","备注"]
[1,"惠州绿色动力环保有限公司","惠阳区","《生活垃圾焚烧污染控制标准》(GB18485-2014)及《惠州市惠阳区榄子垅垃圾综合处理项目生活垃圾焚烧发电项目环境影响报告书》提出的污染物浓度限值","2#焚烧炉废气处理设施排口","2020-05-19",82772,"颗粒物","<20",30,"mg/m3","达标","烟气黑度无相应标准，镉、铅、铜、砷、镍、锰、铬及其化合物无法评价。一氧化碳、铊、锑、钴本站目前无资质。所报数据均折算为11%基准氧含量状态下的排放浓度。   \n"]
[{"$nulls":7},"二氧化硫","<3",100,"mg/m3","达标"]
[{"$nulls":7},"氮氧化物",76,300,"mg/m3","达标"]
[{"$nulls":7},"汞及其化合物",4.2e-5,0.05,"mg/m3","达标"]
[{"$nulls":7},"氯化氢",{"v":3.3,"d":"3.30"},60,"mg/m3","达标"]
[{"$nulls":7},"镉及其化合物","0.0008L","0.05(镉、铊及其化合物以Cd+T1计)","mg/m3","—"]
[{"$nulls":7},"铅及其化合物","0.002L","0.5（锑、砷、铅、铬、钴、铜、锰、镍及其化合物合计）","mg/m3","—"]
[{"$nulls":7},"铜及其化合物","0.0008L"]
[{"$nulls":7},"砷及其化合物",0.00057]
[{"$nulls":7},"镍及其化合物","0.001L"]
[{"$nulls":7},"锰及其化合物","0.0009L"]
[{"$nulls":7},"铬","0.002L"]
[{"$nulls":7},"烟气黑度（林格曼黑度）",0,"—","级","—"]
[{"$nulls":4},"3#焚烧炉废气处理设施排口","2020-05-19",84528,"颗粒物","<20",30,"mg/m3","达标"]
[{"$nulls":7},"二氧化硫","<3",100,"mg/m3","达标"]
[{"$nulls":7},"氮氧化物",91,300,"mg/m3","达标"]
[{"$nulls":7},"汞及其化合物",{"v":3.9e-5,"d":"0.000039"},0.05,"mg/m3","达标"]
[{"$nulls":7},"氯化氢",4.31,60,"mg/m3","达标"]
[{"$nulls":7},"镉及其化合物","0.0008L","0.05(镉、铊及其化合物以Cd+T1计)","mg/m3","—"]
[{"$nulls":7},"铅及其化合物",0.003,"0.5（锑、砷、铅、铬、钴、铜、锰、镍及其化合物合计）","mg/m3","—"]
[{"$nulls":7},"铜及其化合物","0.0008L"]
[{"$nulls":7},"砷及其化合物",0.00053]
[{"$nulls":7},"镍及其化合物","0.001L"]
[{"$nulls":7},"锰及其化合物","0.0009L"]
[{"$nulls":7},"铬","0.002L"]
[{"$nulls":7},"烟气黑度（林格曼黑度）",0,"—","级","—"]
[2,"光大环保能源（博罗）有限公司","博罗县","《生活垃圾焚烧污染控制标准》(GB18485-2014)及《博罗县生活垃圾焚烧发电厂项目环境影响报告书》提出的污染物浓度限值","1#焚烧炉废气处理设施排口","2020-05-26",106210,"颗粒物","<20",30,"mg/m3","达标","烟气黑度无相应标准，镉、铅、铜、砷、镍、锰、铬及其化合物无法评价。一氧化碳、铊、锑、钴本站目前无资质。所报数据均折算为11%基准氧含量状态下的排放浓度。   \n"]
[{"$nulls":7},"二氧化硫",7,100,"mg/m3","达标"]
[{"$nulls":7},"氮氧化物",180,300,"mg/m3","达标"]
[{"$nulls":7},"汞及其化合物",{"v":5e-5,"d":"0.000050"},0.05,"mg/m3","达标"]
[{"$nulls":7},"氯化氢",2.56,60,"mg/m3","达标"]
[{"$nulls":7},"镉及其化合物","0.0008L","0.05(镉、铊及其化合物以Cd+T1计)","mg/m3","—"]
[{"$nulls":7},"铅及其化合物","0.002L","0.5（锑、砷、铅、铬、钴、铜、锰、镍及其化合物合计）","mg/m3","—"]
[{"$nulls":7},"铜及其化合物","0.0008L"]
[{"$nulls":7},"砷及其化合物",0.00243]
[{"$nulls":7},"镍及其化合物","0.001L"]
[{"$nulls":7},"锰及其化合物","0.0009L"]
[{"$nulls":7},"铬","0.002L"]
[{"$nulls":7},"烟气黑度（林格曼黑度）",0,"—","级","—"]
[{"$nulls":4},"3#焚烧炉废气处理设施排口","2020-05-26",146360,"颗粒物","<20",30,"mg/m3","达标"]
[{"$nulls":7},"二氧化硫",4,100,"mg/m3","达标"]
[{"$nulls":7},"氮氧化物",125,300,"mg/m3","达标"]
[{"$nulls":7},"汞及其化合物",3.6e-5,0.05,"mg/m3","达标"]
[{"$nulls":7},"氯化氢",1.84,60,"mg/m3","达标"]
[{"$nulls":7},"镉及其化合物","0.0008L","0.05(镉、铊及其化合物以Cd+T1计)","mg/m3","—"]
[{"$nulls":7},"铅及其化合物","0.002L","0.5（锑、砷、铅、铬、钴、铜、锰、镍及其化合物合计）","mg/m3","—"]
[{"$nulls":7},"铜及其化合物","0.0008L"]
[{"$nulls":7},"砷及其化合物",0.00192]
[{"$nulls":7},"镍及其化合物","0.001L"]
[{"$nulls":7},"锰及其化合物","0.0009L"]
[{"$nulls":7},"铬","0.002L"]
[{"$nulls":7},"烟气黑度（林格曼黑度）",0,"—","级","—"]
[3,"光大环保能源（惠东）有限公司","惠东县","《生活垃圾焚烧污染控制标准》(GB18485-2014)及《惠东生活垃圾焚烧发电项目环境影响报告书》提出的污染物浓度限值","1#焚烧炉废气处理后排口","2020-05-27",139749,"颗粒物","<20",30,"mg/m3","达标","烟气黑度无相应标准，铜、砷、镍、锰、铬及其化合物无法评价。一氧化碳、铊、锑、钴本站目前无资质。所报数据均折算为11%基准氧含量状态下的排放浓度。   \n"]
[{"$nulls":7},"二氧化硫","<3",100,"mg/m3","达标"]
[{"$nulls":7},"氮氧化物",85,300,"mg/m3","达标"]
[{"$nulls":7},"汞及其化合物",{"v":0.00011,"d":"0.000110"},0.05,"mg/m3","达标"]
[{"$nulls":7},"氯化氢",3.58,60,"mg/m3","达标"]
[{"$nulls":7},"镉及其化合物","0.0008L","0.05(镉、铊及其化合物以Cd+T1计)","mg/m3","—"]
[{"$nulls":7},"铅及其化合物","0.002L","0.5（锑、砷、铅、铬、钴、铜、锰、镍及其化合物合计）","mg/m3","—"]
[{"$nulls":7},"铜及其化合物","0.0008L"]
[{"$nulls":7},"砷及其化合物",0.00127]
[{"$nulls":7},"镍及其化合物","0.001L"]
[{"$nulls":7},"锰及其化合物","0.0009L"]
[{"$nulls":7},"铬","0.002L"]
[{"$nulls":7},"烟气黑度（林格曼黑度）",0,"—","级","—"]
[{"$nulls":4},"2#焚烧炉废气处理后排口","2020-05-27",134137,"颗粒物","<20",30,"mg/m3","达标"]
[{"$nulls":7},"二氧化硫","<3",100,"mg/m3","达标"]
[{"$nulls":7},"氮氧化物",117,300,"mg/m3","达标"]
[{"$nulls":7},"汞及其化合物",9.3e-5,0.05,"mg/m3","达标"]
[{"$nulls":7},"氯化氢",2.78,60,"mg/m3","达标"]
[{"$nulls":7},"镉及其化合物","0.0008L","0.05(镉、铊及其化合物以Cd+T1计)","mg/m3","—"]
[{"$nulls":7},"铅及其化合物","0.002L","0.5（锑、砷、铅、铬、钴、铜、锰、镍及其化合物合计）","mg/m3","—"]
[{"$nulls":7},"铜及其化合物","0.0008L"]
[{"$nulls":7},"砷及其化合物",0.00138]
[{"$nulls":7},"镍及其化合物","0.001L"]
[{"$nulls":7},"锰及其化合物","0.0009L"]
[{"$nulls":7},"铬","0.002L"]
[{"$nulls":7},"烟气黑度（林格曼黑度）",0,"—","级","—"]
[4,"光大环保能源（龙门）有限公司","龙门县","《生活垃圾焚烧污染控制标准》(GB18485-2014)及《龙门县城乡生活垃圾无缝对接一体化处理项目——资源热力电厂项目环境影响报告书》提出的污染物浓度限值","1#焚烧炉废气处理设施排口","2020-06-16",49339,"颗粒物","<20",10,"mg/m3","—","烟气黑度无相应标准，镉、铅、铜、砷、镍、锰、铬及其化合物无法评价。低浓度颗粒物、一氧化碳、铊、锑、钴本站目前无资质。所报数据均折算为11%基准氧含量状态下的排放浓度。   \n"]
[{"$nulls":7},"二氧化硫","<3",100,"mg/m3","达标"]
[{"$nulls":7},"氮氧化物",199,250,"mg/m3","达标"]
[{"$nulls":7},"汞及其化合物",{"v":3.8e-5,"d":"0.000038"},0.05,"mg/m3","达标"]
[{"$nulls":7},"氯化氢",6.27,60,"mg/m3","达标"]
[{"$nulls":7},"镉及其化合物","0.0008L","0.05(镉、铊及其化合物以Cd+T1计)","mg/m3","—"]
[{"$nulls":7},"铅及其化合物","0.002L","0.5（锑、砷、铅、铬、钴、铜、锰、镍及其化合物合计）","mg/m3","—"]
[{"$nulls":7},"铜及其化合物","0.0008L"]
[{"$nulls":7},"砷及其化合物",0.00089]
[{"$nulls":7},"镍及其化合物","0.001L"]
[{"$nulls":7},"锰及其化合物","0.0009L"]
[{"$nulls":7},"铬","0.002L"]
[{"$nulls":7},"烟气黑度（林格曼黑度）",0,"—","级","—"]
[{"$nulls":4},"2#焚烧炉废气处理设施排口","2020-06-16",48509,"颗粒物","<20",10,"mg/m3","—"]
[{"$nulls":7},"二氧化硫","<3",100,"mg/m3","达标"]
[{"$nulls":7},"氮氧化物",231,250,"mg/m3","达标"]
[{"$nulls":7},"汞及其化合物",3.6e-5,0.05,"mg/m3","达标"]
[{"$nulls":7},"氯化氢",14.2,60,"mg/m3","达标"]
[{"$nulls":7},"镉及其化合物","0.0008L","0.05(镉、铊及其化合物以Cd+T1计)","mg/m3","—"]
[{"$nulls":7},"铅及其化合物","0.002L","0.5（锑、砷、铅、铬、钴、铜、锰、镍及其化合物合计）","mg/m3","—"]
[{"$nulls":7},"铜及其化合物","0.0008L"]
[{"$nulls":7},"砷及其化合物",0.00096]
[{"$nulls":7},"镍及其化合物","0.001L"]
[{"$nulls":7},"锰及其化合物","0.0009L"]
[{"$nulls":7},"铬","0.002L"]
[{"$nulls":7},"烟气黑度（林格曼黑度）",0,"—","级","—"]
[5,"惠州广惠能源有限公司","惠城区","《生活垃圾焚烧污染控制标准》(GB18485-2014)及《惠州市区垃圾焚烧发电项目—芦洲林果场选址环境影响报告书》提出的污染物浓度限值","1#焚烧炉废气处理后排口","2020-05-26",97950,"颗粒物","<20",30,"mg/m3","达标","烟气黑度无相应标准，铜、砷、镍、锰、铬及其化合物无法评价。一氧化碳、铊、锑、钴本站目前无资质。所报数据均折算为11%基准氧含量状态下的排放浓度。   \n"]
[{"$nulls":7},"二氧化硫","<3",100,"mg/m3","达标"]
[{"$nulls":7},"氮氧化物",96,200,"mg/m3","达标"]
[{"$nulls":7},"汞及其化合物",{"v":4.1e-5,"d":"0.000041"},0.05,"mg/m3","达标"]
[{"$nulls":7},"氯化氢",7.42,30,"mg/m3","达标"]
[{"$nulls":7},"镉及其化合物","0.0008L","0.05(镉、铊及其化合物以Cd+T1计)","mg/m3","—"]
[{"$nulls":7},"铅及其化合物","0.002L","0.5（锑、砷、铅、铬、钴、铜、锰、镍及其化合物合计）","mg/m3","—"]
[{"$nulls":7},"铜及其化合物","0.0008L"]
[{"$nulls":7},"砷及其化合物",0.00062]
[{"$nulls":7},"镍及其化合物","0.001L"]
[{"$nulls":7},"锰及其化合物","0.0009L"]
[{"$nulls":7},"铬","0.002L"]
[{"$nulls":7},"烟气黑度（林格曼黑度）",0,"—","级","—"]
[{"$nulls":4},"2#焚烧炉废气处理后排口","2020-05-26",105259,"颗粒物","<20",30,"mg/m3","达标"]
[{"$nulls":7},"二氧化硫","<3",100,"mg/m3","达标"]
[{"$nulls":7},"氮氧化物",88,200,"mg/m3","达标"]
[{"$nulls":7},"汞及其化合物",3.9e-5,0.05,"mg/m3","达标"]
[{"$nulls":7},"氯化氢",5.83,30,"mg/m3","达标"]
[{"$nulls":7},"镉及其化合物","0.0008L","0.05(镉、铊及其化合物以Cd+T1计)","mg/m3","—"]
[{"$nulls":7},"铅及其化合物","0.002L","0.5（锑、砷、铅、铬、钴、铜、锰、镍及其化合物合计）","mg/m3","—"]
[{"$nulls":7},"铜及其化合物","0.0008L"]
[{"$nulls":7},"砷及其化合物",0.00059]
[{"$nulls":7},"镍及其化合物","0.001L"]
[{"$nulls":7},"锰及其化合物","0.0009L"]
[{"$nulls":7},"铬","0.002L"]
[{"$nulls":7},"烟气黑度（林格曼黑度）",0,"—","级","—"]
[{"$nulls":4},"3#焚烧炉废气处理后排口","2020-05-26",100552,"颗粒物","<20",30,"mg/m3","达标"]
[{"$nulls":7},"二氧化硫","<3",100,"mg/m3","达标"]
[{"$nulls":7},"氮氧化物",66,200,"mg/m3","达标"]
[{"$nulls":7},"汞及其化合物",3.9e-5,0.05,"mg/m3","达标"]
[{"$nulls":7},"氯化氢",9.28,30,"mg/m3","达标"]
[{"$nulls":7},"镉及其化合物","0.0008L","0.05(镉、铊及其化合物以Cd+T1计)","mg/m3","—"]
[{"$nulls":7},"铅及其化合物","0.002L","0.5（锑、砷、铅、铬、钴、铜、锰、镍及其化合物合计）","mg/m3","—"]
[{"$nulls":7},"铜及其化合物","0.0008L"]
[{"$nulls":7},"砷及其化合物",0.00056]
[{"$nulls":7},"镍及其化合物","0.001L"]
[{"$nulls":7},"锰及其化合物","0.0009L"]
[{"$nulls":7},"铬","0.002L"]
[{"$nulls":7},"烟气黑度（林格曼黑度）",0,"—","级","—"]