{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["废水"],"not_rendered":{"external_links":1,"defined_names":2},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"废水","index":0,"n_rows":9,"n_cols":17,"rows_kept":9,"merged":[[0,0,0,16],[1,5,1,16],[4,0,4,2],[5,0,5,2],[7,0,7,2],[8,0,8,2]],"flags":["formulas_cached_only"]}
["附件3：                惠州市2020年8月生活垃圾处理企业废水监督性监测结果（2家）"]
[{"$nulls":5},"单位:毫克/升（除PH值无量纲，色度为倍外）"]
["企业名称","监测日期","监测点位","pH值","悬浮物","化学需氧量","五日生化需氧量","氨氮","总氮","总磷","总铬","六价铬","砷","镉","铅","汞","色度"]
["惠州市市容环境卫生管理局(惠州市垃圾处理场)","2020-07-22","渗滤液处理后排口",8.13,7,26,5.9,0.42,0.71,"0.01L","0.03L","0.004L","0.0003L","0.003L","0.03L","0.00004L",2]
["评价",null,null,"达标","达标","达标","达标","达标","达标","达标","达标","达标","达标","达标","达标","达标","达标"]
["《生活垃圾填埋场污染控制标准》GB16889-2008、广东省地方标准《水污染物排放限值》DB44/26-2001",null,null,"6—9",20,90,20,10,40,0.5,0.1,0.05,0.1,0.01,0.1,0.001,40]
["惠东县垃圾填埋场","2020-07-29","废水排放口",7.04,6,9,{"v":2,"d":"2.0"},2.62,7.14,"0.01L","0.03L","0.004L","0.0003L","0.003L","0.03L","0.00004L",2]
["评价",null,null,"达标","达标","达标","达标","达标","达标","达标","达标","达标","达标","达标","达标","达标","达标"]
["《生活垃圾填埋场污染控制标准》GB16889-2008、广东省地方标准《水污染物排放限值》DB44/26-2001",null,null,"6—9",30,90,20,10,40,3,0.1,0.05,0.1,0.01,0.1,0.001,40]